## Sheet1
ITEM |  | USE | SIZE | NUMBER OF | TYPE | LENGTH (ft) or | Rob's notes
1/2/2011 supersedes 12/29/10 |  |  |  | CONDUTORS |  | quantity
(Cu)
1 | Drop for SMUD to metered fused Main disconnect (item 2a) |  |  | 4 | THHN/THWN | 12 | I don't know if we supply this or if SMUD does.
2a | Meter Socket, 3 phase |  | 200 Amp | NEMA 3R | Smud type with test bypass | 1 | Does this need to be nema 4 or nema 3R?
2b | combined with item 2a & 2c |  | n/a | n/a | n/a | n/a
2c | Switch, Main power disconnect switch (200A, 240VAC, 3phase ) |  | NEMA 3R | 5 feed | 200A,240vac3phase | 1
2d | wire, Ground wire for main disconnect |  | #2 | 1 | Solid bare | 50 ft
2e | Conduit, Ground conduit for main disconnect |  | 3/4 in | 1 | EMT | 50 ft
2f | wire, SMUD connection point to meter socket |  | 3/0 awg | 4 | THHN/THWN | 20' ea | guessing on the length
2g | wire, meter socket to disconnect switch to SE panel |  | 3/0 awg | 4 | THHN/THWN | 15' | guessing on the length
2h | wire, ground between iceland and american ice |  | #2 awg | 1 | bare | 100' | guessing on the length
3 | Conduit, Connect Main power distrubution pnl to distrubution pnl "SW" |  | 2 in |  | EMT | 1
4 | Panel, Main power distrubution panel "SE" (200A, 240VAC, 3phase,4wire ) |  | NEMA 3R | 42 circ | 200A,240vac3phase | 1
4a | Bkrs for panel "SE" |  | 60A |  | 60A, 3P | 2
4b | Bkrs for panel "SW", GFI |  | 20A |  | 20A, 1P | 11 | I think we only need 5 for SW, but we need 4 on SE and 4 on NE
5 | Conduit from existing 2in rigid conduit to new 2in EMT |  | 2in |  | PVC | 60 ft
5a | Conduit from new 2in PVC up to new panel "NE" |  | 2in |  | EMT | 10 ft | can this be 2" or does it have to match the 1-1/2" that it connects to?
6 | Wire from pnl "SE" to pnl "SW" |  | #6 AWG | 5 | THHN/THWN | 150 ft | I think we only need #6 for 60 amp
7 | Panel "SW" Located inside back of rink nr. Rear exit (125A, 240VAC,3phase) |  | NEMA 3R | 42 Circuit | 125A,240VAC,3phase | 1
7a | Bkrs for panel "SW", GFI |  | 20A |  | 20A, 1P | 5
8 | Wire from pnl "SE" to pnl "NE" |  | #6 AWG | 5 | THHN/THWN | 160 ft
9 | Conduit from existing 1-1/2in rigid conduit to new 1-1/2in EMT |  | 1-1/2in | 5 #6AWG | PVC | 40 ft
10 | Panel "NE" Located inside front of rink nr. Front exit (125A, 240VAC,3phase) |  | NEMA 3R | 42 Circuit | 125A,240VAC,3phase | 1
10a | Bkrs for panel "NE", GFI |  | 20A |  | 20A, 1P | 7
11 | Conduit from new 1-1/2in 1-1/2 PVC up to new panel "NE" |  | 1-1/2in | 5 #6AWG | EMT | 10 ft
12 | wire, Gas pipe ground wire |  | #6AWG | 1 | solid bare | 20 ft
13 | Conduit, Gas pipe conduit from pnl "NE" to gas pipe |  | 3/4 in | 1 | EMT | 20 ft
13a | wire, Gas pipe ground wire pipe connector |  | 3/4 in | 1 | pipe to wire connector | 1
14 | wire, Water pipe ground |  | #6 | 1 | solid bare | 180 ft
15a | Conduit, Water pipe ground wire conduit from 3/4 in EMT to water pipe |  | 3/4 in | 1 | PVC | 30 ft
15 | Conduit, Water pipe ground wire conduit from pnl "SW" to 3/4 in PVC (item 16) |  | 3/4 in | 1 | EMT | 30 ft
16 | Wire, Water pipe ground wire pipe connector |  | 3/4 in | 1 | pipe to wire connector | 1
17 | Anchors for power panels "SW", "SE", "NE" |  | 1/2 in |  | "red heads" | 16
18 | Anchors for 2" EMT (conduit clamps for concrete) |  | 2 in |  | std 2" EMT | 1 doz
19 | Anchors for 1-1/2" EMT (for conduit clamps for concrete) |  | 1-1/2 in |  | std 1-1/2 EMT | 1 doz
20 | Anchors for 3/4 " EMT ( for conduit clamps for concrete) |  | 3/4 in |  | std 3/4 EMT | 4 doz
21 | Lighting, Exit "XL" , Greentorch XWLC |  |  |  | Greentorch XWLC | 2 | in-stock
22 | Lighting, Exit "EL" , Greentorch WVHEL |  |  |  | Greentorch WVHEL | 3 | ordered
23 | Lighting, Outdoor light "OL", wall pack-e-conolight E-WP1F421Z |  |  |  | Econolight E-WP1F421Z | 8 | in-stock
24 | Lighting, Flood light "FL" pole mount, item 46 for poles |  |  |  | Econolight E-HR4P25QZ | 5 | in-stock
25 | Junction box "j", 4x4 or 8x8? |  | 4x4 |  | ? | 14
26 | Lighting, switch box , 3 gang, rink perimeter lighting inside. |  | 3 gang |  | 3 gang, weathertight, 3/4" | 1
27 | Lighting, switch box, 1 gang, rink perimeter lighting outside. |  | duplex |  | 1 gang, weathertight, 3/4" | 1
28 | Lighting, switch box, 2 gang, "ICELAND" lighting and pagoda control box. |  | quad |  | 2 gang, weathertight, 3/4" | 1
29 | Conduit, 3/4" EMT, 40 ft from panel "NE" to sign switch (item 28) |  | 3/4" |  | EMT | 40 ft
30 | Wire, #12AWG Cu, THHN/THWN, black, sign power from pnl "NE". |  | #12 AWG | 1 | #12AWG THHN/THWN | 40 ft
31 | Wire, #12AWG Cu, THHN/THWN,white, sign power from pnl "NE". |  | #12 AWG | 1 | #12AWG THHN/THWN | 40 ft
32 | Wire, #12AWG Cu, THHN/THWN, green, sign power from pnl "NE". |  | #12 AWG | 1 | #12AWG THHN/THWN | 40 ft
33 | Receptical box, 4x4, weather tight, power from pnl "SW". See item 52 |  | #12 AWG |  | 4X4, weathertight, 3/4" | 2
34 | Receptical box, 2x2, weather tight, power from pnl "SW". |  | #12 AWG |  | 2x2, weathertight, 3/4" | 1
35 | Conduit, 3/4" SCH40 PVC, to item 34 |  | 3/4" |  | SCH40, PVC | 40 ft
36 | Wire, #12AWG Cu, THHN/THWN, black, sign power from pnl "SW". |  | #12 AWG | 1 | #12AWG THHN/THWN | 40 ft
37 | Wire, #12AWG Cu, THHN/THWN,white, sign power from pnl "SW". |  | #12 AWG | 1 | #12AWG THHN/THWN | 40 ft
38 | Wire, #12AWG Cu, THHN/THWN, green, sign power from pnl "SW". |  | #12 AWG | 1 | #12AWG THHN/THWN | 40 ft
39 | Conduit, 3/4" EMT, power from 4x4 box switch to all "FL", NE side, 2 runs of 120 ft. |  | #12 AWG |  | EMT | 240 ft
40 | Conduit, 3/4" EMT, power from 4x4 box switch to all "FL", SW side, 2 runs of 80 ft. |  | #12 AWG |  | EMT | 160 ft
41 | Wire, #12AWG Cu, THHN/THWN, black, power for "FL", 2 runs of 200 ft. |  | #12 AWG | 1 | #12AWG THHN/THWN | 400 ft
42 | Wire, #12AWG Cu, THHN/THWN, white, power for "FL", 2 runs of 200 ft. |  | #12 AWG | 1 | #12AWG THHN/THWN | 400 ft
43 | Wire, #12AWG Cu, THHN/THWN, green, power for "FL", 2 runs of 200 ft. |  | #12 AWG | 1 | #12AWG THHN/THWN | 400 ft
44 | Nipples, 2", for box entry items 2c,47 |  | 3/4 in |  | 3/4" EMT compression type | 12
45 | Couplers, 3/4" for connection of 3/4"conduit, items 29,35,39 & 40 |  | 3/4 in |  | 3/4" EMT compression type | 50
46 | Lighting, poles for "FL" (item 24) |  | 2" dia |  | 2" dia steel, 20 ft long (water pipe) | 5 | These can be rigid conduit or water pipe. The actual OD is 2-3/8", I think. Water is probably easier.
47 | Lighting, pole bracing kits |  | 2" |  |  | 5 | These are the brace kits that normally go on periscope service inlets.
48 | Nipples, 1-1/2", for box entry on items 10 &4 |  | 1-1/2 in |  | 1-1/2 compression type | 2
49 | Nipples, 3/4" for box entry items 7,10,4,29,34,35,36,37,38,39,40,41,42,43 |  | 3/4" |  | 3/4" compression type | 100
50 | Conduit, 1" EMT, from LED sign switch to sign |  | 1" |  | EMT | 10 ft
51 | Receptical box, weathertight, 3/4" entry. See item 33 |  |  |  | 2x2, weathertight, 3/4" | 12
52 | Receptical box, weathertight, 3/4" entry. Outside 4x4 nr "SVC" |  |  |  | 4X4, weathertight, 3/4" | 1
53 | Unistrut for attaching panels "SVC", "SE", "SW", & "NE" |  |  |  | 20 ft unistrut | 20 ft
54 | Flex, 3/4 weathertight, for connection frm "J" to "FL"s, "XL"s &"EL"s |  |  |  | 30 feet | 30 ft
55 | Conduit " Jakes" for flex fittings, item54 |  |  |  | EMT | 4 doz
56 | Conduit, 1/2", EMT, conncetion from "J" to "FL" |  |  |  | EMT | 50 ft
57 | 6" x 6" x 48" or 60" NEMA 3R gutter for SE wall between SE panel and conduits
58 | copper ground bus for american ice, approx. 12 - 16" long
59 | box for ground bus at american ice
Note on A33: x: