(X)	Please revise all submittal documents to comply with the following comments.

(X)	A complete plan check cannot be complete without the information requested.

(X)	All resubmittals require a written summary of changes in response to all comments.  The written summary should reference all revised sheets, calculation pages, and details.

Please be aware that the following general comments may apply to your project:

A.	All plan review time beyond the 3rd cycle of review will be charged $140 per hour.

B.	An application for a permit for any proposed work shall be deemed to have been abandoned 180 days after the date of filing (submittal date) per CBC Section 105.3.2. The abandoned permit will be expired and new fees must be paid. The applicant may request a 90-day extension by submitting a letter to the Chief Building Official, demonstrating justifiable cause, prior to the expiration date.

http://www.cityofsacramento.org/dsd/building/plan-review/survey.cfm

CTRL + Click on the link above to fill out the customer survey

| Item # | # Comments | Detail / Sheet |
| --- | --- | --- |
| 1 | Provide grounding electrode at new SVC panel and ty grounding electrode from new service to existing service at ice plant in order to provide common ground between both buildings. | E |
| 2 | Provide one line diagram for electrical service thru subpanels. Show conduit and conductor size. Bond all gas and water as well as metal to service panel. | E |
| 3 | .Provide SMUD commitment letter for new service. | E |
| 4 | Provide title 24 outdoor lighting forms. List all fixture types. If flood light type is being used show fixture cut sheet for being cut-off rated. Provide support for new flood light detail. How are these lights to be controlled? Provide photo metrics for lighting. |  |
| 5 | Provide exit and egress lighting. Egress lighting will be required inside building. Provide 90 min. battery backup for egress lighting. Provide egress lighting at exit in alley and between buildings. Provide egress path on layout plans. | E |
| 6 | Provide information for reconnecting existing and new signs. Show dedicated circuits and disconnects for these signs. Provide platform at sign panel board for maintenance. Use approved raceways and method of installation. | E |
| 7 | Provide info for requiring new electrical outlet in all areas. What are these outlets to be used for? You are showing 3 locations with 4 outlets each. Provide loads for all outlets on panel schedule. Provide circuit # for all outlets, sign and lighting. Provide elevation for all outlets. | E |
| 8 | Provide elevation of panels and show how you are going to have proper working clearance as per NEC 110.26. Not maximum height for breakers and switches. | E |
| 9 | Wiring review for rink wiring only. No support buildings or other wiring has been submitted. |  |
| 10 | This review is for building without roof and no heating. Further permits to be applied for as rink is increasingly remodeled. Further comments may be required due to your response. |  |
| 11 | This rink should provide facilities and may require lights. Show lights and means of control. |  |

Go to www.cityofsacramento.org/dsd   “Lookup a permit application or property” to review the status of your plan check on line.