## Sheet1
LOAD CALCULATION
PANEL SW
|  |  |  | KVA | DESCRIPTION
1 |  |  |  | KVA | CONTINUOUS NON-MOTOR
0.25 |  |  |  | KVA | 25% CONTINUOUS NON-MOTOR
1 |  |  |  | KVA | NON-CONTINUOUS
10 |  |  |  | KVA | RECEPTACLE (FIRST 10KVA)
4.6 |  |  |  | KVA | RECEPTACLE (BALANCE AT 50%)
0.5 |  |  |  | KVA | MOTOR LOAD
0.125 |  |  |  | KVA | 25% OF LARGEST MOTOR
0 |  |  |  | KVA | KITCHEN EQUIPMENT
0 |  |  |  | KVA | HOTEL/MOTEL DEMAND
0 |  |  |  | KVA | ARC WELDERS
0 |  |  |  | KVA | RESISTANCE WELDERS
17.475 |  |  |  |  | LOAD KVA
42.8309 |  |  |  |  | AMPS AT 240 V 3 PHASE
LOAD CALCULATION
PANEL NE
|  |  |  | KVA | DESCRIPTION
1 |  |  |  | KVA | CONTINUOUS NON-MOTOR
0.25 |  |  |  | KVA | 25% CONTINUOUS NON-MOTOR
1 |  |  |  | KVA | NON-CONTINUOUS
10 |  |  |  | KVA | RECEPTACLE (FIRST 10KVA)
4.6 |  |  |  | KVA | RECEPTACLE (BALANCE AT 50%)
0 |  |  |  | KVA | MOTOR LOAD
0 |  |  |  | KVA | 25% OF LARGEST MOTOR
0 |  |  |  | KVA | KITCHEN EQUIPMENT
0 |  |  |  | KVA | HOTEL/MOTEL DEMAND
0 |  |  |  | KVA | ARC WELDERS
0 |  |  |  | KVA | RESISTANCE WELDERS
16.85 |  |  |  |  | LOAD KVA
41.299 |  |  |  |  | AMPS AT 240 V 3 PHASE
LOAD CALCULATION
PANEL SE
Total | SE | SW | NW | KVA | DESCRIPTION
4 | 0 | 0 | 0 | KVA | CONTINUOUS NON-MOTOR
1 | 0 | 0 | 0 | KVA | 25% CONTINUOUS NON-MOTOR
2 | 0 | 0 | 0 | KVA | NON-CONTINUOUS
30 | 0 | 0 | 0 | KVA | RECEPTACLE (FIRST 10KVA)
14.2 | 0 | 0 | 0 | KVA | RECEPTACLE (BALANCE AT 50%)
0.5 | 0 | 0 | 0 | KVA | MOTOR LOAD
0.125 | 0 | 0 | 0 | KVA | 25% OF LARGEST MOTOR
0 | 0 | 0 | 0 | KVA | KITCHEN EQUIPMENT
0 | 0 | 0 | 0 | KVA | HOTEL/MOTEL DEMAND
0 | 0 | 0 | 0 | KVA | ARC WELDERS
0 | 0 | 0 | 0 | KVA | RESISTANCE WELDERS
51.825 | 0 | 0 | 0 |  | LOAD KVA
127.0221 | 0 | 0 | 0 |  | AMPS AT 240 V 3 PHASE
Note on A7: Rob Kerth: 4 @ 20 A
Note on A25: Rob Kerth: 4 @ 20 A